## Slide 1: 350 MW Wind + Solar Hybrid Power Generation Project at Jhimpir, Thatta.
Directorate of Alternative Energy,
Government of Sindh

## Slide 2: Project Details:
  Technology: 250 MW Wind + 100 MW Solar
  Location: Jhimpir, Thatta
  Land Available: 2,291 Acres in Deh Kohistan 7/1 Tapo Jhampir, District Thatta. (Reserved)
  Implementation Model: Business to Business (B2B)
  Potential Buyer: Industrial Buyers in Karachi, Nooriabad, Hyderabad

## Slide 3: Parameters
Expected Annual Generation: app. 940 GWh/Anum
  App. 2.57 GWh/day
Project EPC Cost: Approx USD 365 Million or Rs.102.2 Billion @ Rs.280/USD
  Equity: 100% GoS
  Or 20% Equity & 80% debt (commercial banks or GoS)
Project Life: 25 Years
COD: 20 months (from the date of Financial Close)

## Slide 4: Project Proposed Land

## Slide 5
Project | Size | Latitude | Longitude
SREC 100 MW Wind Power Project | 2291 Acres | 25° 3'39.23"N | 67°46'16.84"E
 |  | 25° 3'31.32"N | 67°46'8.05"E
 |  | 25° 0'29.87“N | 67°49'49.93"E
 |  | 25° 0'20.08"N | 67°49'39.51"E
 |  | 25° 4'7.05"N | 67°46'43.74"E
 |  | 25° 4'0.06"N | 67°46'35.72"E
 |  | 25° 0'55.29"N | 67°50'21.20"E
 |  | 25° 0'48.11"N | 67°50'13.26"E
Project Proposed Land

## Slide 6: Project Proposed Land
Land was approved by Scrutiny Committee headed by Chairman LU Department dated 6.11.2015
Despite communication several times, allotment order yet to be issued by BoR.
Rates as approved by the Scrutiny Committee are:
  Rs.3000 per acre per annum for 1st 10 Years = Rs. 68.73 Million
  Rs.5000 per acre per annum for next 10 Years = Rs. 114.55 Million
  Rs.8000 per acre per annum for further 10 Years = Rs. 183.28 Million
Total of Rs.366.56 Million to be paid for Land. However, initially an amount of Rs.67.73 million will be paid, remaining amount will be paid later in 2 installments i.e. at the start of each 10 years period.

## Slide 7
Wind Farm Capacity | 250 MW
Plant Capacity Factor | 35%
Estimated Output | App. 87.5 MW
Estimated Annual Generation | 766 GWh per Annum.
Turbines to be used | 36 Turbines each of 7 MW
Manufacturer (To be finalized after competitive bidding) | Goldwind or Gamesa or Vestas Denmark or CSIC China or HydroChina Corporation or Nordex Germany (subject to success in competitive bidding)
Wind EPC Cost | 1.20 Million USD/MW
Total Cost | 300 Million USD
Project Details: Wind

## Slide 8
Solar Capacity | 100 MW
Plant Capacity Factor | 20%
Estimated Output | App. 20 MW
Estimated Annual Generation | 175.2 GWh
Solar PV Panels to be used | 142858 Panels each of 700 W Inverters 300 KW or 4 – 5 MW (Depends upon Design of Power Plant)
Manufacturer | Longi, JS, Canadian Solar, etc… To be finalized after competitive bidding
Soar PV EPC Cost | 0.65 Million USD/MW
Total EPC | 65 Million USD/MW
Project Details: Solar

## Slide 9
Project Details: Evacuation Plan by STDC

## Slide 10
Transmission lines Capacity | 350 MW Evacuation
Total Project Cost | 19.865 Billion
Financing Structure | 20% Equity: 80% Debt
Return on Equity | 20%
Levelized Tariff for Wheeling over 25 Years | Rs. 5.1395
Project Details: Evacuation Plan by STDC

## Slide 11
Plant Capacity | 350 MW
Estimated Annual Generation | 947.1 GWh
Total Project Cost | Rs. 368.17 Billion
Financing Structure | 20% Equity : 80% Debt
Project Life | 25 Years
Total Project Cost | USD 365 Million or Rs. 102.2 Billion @ Rs.280/USD
Levelized Tariff Generation | ~Rs.13.3/Unit
Levelized Tariff Transmission | 5.1395
Total Levelized Tariff of the Project | Rs.18.45/Unit
Project Details: Wind+Solar Hybrid

## Slide 12
Solar PV and Wind Hybrid have time frames where both resources are available lesser than the required Power.
Both resources are intermittent and can create voltage stabilization and frequency drop issues
In order to improve the output profile of Solar & Wind Hybrid Power Plants, Battery Energy Storage Systems are added.
BESS charges energy during excess generation period and discharges as and when required to provide a stable power output profile
Hybrid Power System Solar PV – Wind - BESS

## Slide 13: Following Cases are studied
01
02
03
Case 2
250MW Wind + 100MW Solar + 100/300MWh BESS
Case 1
: 250MW Wind + 100MW Solar
Case 3
300MW Wind + 150MW Solar + 30MW/150MWh BESS

## Slide 14: Case 1 250MW Wind + 100MW Solar
Results Case 1 250MW Wind + 100MW Solar
Total Generation Output = 1138 MWh per annum
Capacity Factor = 52%
Transmission Evacuation Capacity is kept at 350MW
No. of hours during which the output is greater than 300MW is only 19 hours, No. of hours during which the output is greater than 200MW is 2370
Case 1is assumed as a single block
Larger BESS would be required to ensure more smooth continuous supply of energy levels

## Slide 15: Case 2 250MW Wind + 100MW Solar + 100 / 300 MWh BESS
Results Case 2
Total Generation Output = 1136 MWh per annum
Capacity Factor = 51.6%
Transmission Evacuation Capacity is kept at 250MW to allow for charging of BESS above 250MW
No. of hours during which the output is greater than 200MW is 2424
Case 2 is assumed as a single block
This means with a 250MW/100MW Hybridization a 100/300MWh battery is enough to deliver the energy continuously for above 200MW for 2424 hour.
A further increase in installed capacity of Wind and Solar would be required to ensure continuous delivery of power above 250MW

## Slide 16: Case 3 300MW Wind + 150MW Solar + 3* (50 / 100) MWh BESS
This case is to be developed in three blocks each of following size
  (100MW Wind + 50MW Solar + 50MW/100MWh BESS) X 3
This will ensure a relatively smoother output and easier to manage
The transmission evacuation capacity can be governed by 100MW of wind- ( Total of 300MW)
The target is that each power plant shall deliver 100MW power continuously for longer period and 50MW stable output
Total Generation Output = 468.22 MWh per annum ( out of 470MWh)
Capacity Factor = 54% ( with 300MW evacuation capacity)
Transmission Evacuation Capacity is kept at 100MW to allow for charging of BESS above 100MW
No. of hours during which the output is greater than 50MW is 4242 which is 48.5% and greater than 80MW for 2549 hours

## Slide 17: Pakistan – COMPARISON WITH SELECT COUNTRIES
  Based on the trends observed in countries with a developed solar energy market, such as Germany and the USA, the solar adaptation process can be mapped along a curve with various stages based on the stage of solar adoption for end-consumers of solar energy.
Adoption stage
Take-off point
2012
2014
2015
2011
2005
2000
Solar energy adoption cycle by country and introduction of net-metering
Note:
*The years represent the introduction of net-metering policy by the Government.
** The stages apply to companies that are the end-consumers of solar energy within the C&I segment.
Note: In Germany, the net-metering concept was not introduced until 2000. The initial growth was driven by other incentives and benefits such as subsidies and feed-in tariffs.
2019

## Slide 18: Hybrid – Wind + Solar
Resource Maps – Wind & Solar -Jhimpir
Details of Solar Resource
Details of Wind Resource
Details of Solar Resource

## Slide 19: Simulation: Wind + Solar Hybrid (Winters)
Chart: January
| 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23
WIND Average Gross Power | 26.9043 | 28.0735 | 28.8731 | 30.2852 | 32.0564 | 31.507 | 31.1272 | 28.758 | 27.9123 | 19.3189 | 17.8782 | 18.5748 | 17.2474 | 15.1272 | 14.5827 | 16.2069 | 18.6038 | 23.3528 | 27.9156 | 29.4131 | 28.883 | 27.357 | 24.3081 | 25.8367
SOLAR Average Gross Power | -0.038 | -0.038 | -0.038 | -0.038 | -0.038 | -0.038 | -0.038 | 0.0010323 | 8.7634 | 17.6962 | 18.8114 | 19.2495 | 18.9692 | 18.8536 | 18.8373 | 18.2194 | 12.0206 | 1.4345 | -0.038 | -0.038 | -0.038 | -0.038 | -0.038 | -0.038
WIND+SOLAR Average Gross Power | 26.8663 | 28.0355 | 28.8351 | 30.2472 | 32.0184 | 31.469 | 31.0892 | 28.759 | 36.6757 | 37.0151 | 36.6896 | 37.8243 | 36.2166 | 33.9809 | 33.42 | 34.4263 | 30.6244 | 24.7873 | 27.8776 | 29.3751 | 28.845 | 27.319 | 24.2701 | 25.7987

## Slide 20: Simulation: Wind + Solar Hybrid (Summers)
Chart: July
| 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23
Wind | 40.5688 | 39.7976 | 38.5918 | 36.7345 | 35.3792 | 35.0422 | 35.8865 | 34.5923 | 34.5981 | 35.5967 | 35.8577 | 36.1627 | 35.6595 | 36.5073 | 36.8483 | 38.6785 | 41.5521 | 43.1142 | 45.2265 | 45.3073 | 43.6668 | 42.533 | 41.6474 | 40.7224
Solar | -0.038 | -0.038 | -0.038 | -0.038 | -0.038 | -0.038 | 2.3339 | 8.0994 | 12.424 | 14.8295 | 18.1599 | 17.7941 | 18.2794 | 18.2334 | 16.5971 | 14.9303 | 11.9768 | 8.04 | 2.4655 | -0.038 | -0.038 | -0.038 | -0.038 | -0.038
Hybrid | 40.5308 | 39.7596 | 38.5538 | 36.6965 | 35.3412 | 35.0042 | 38.2204 | 42.6917 | 47.022 | 50.4261 | 54.0177 | 53.9567 | 53.9389 | 54.7407 | 53.4454 | 53.6088 | 53.5289 | 51.1543 | 47.6919 | 45.2693 | 43.6288 | 42.495 | 41.6094 | 40.6844

## Slide 21: Generation – Each WTG Option
Chart: KWh
| Siemens Gamesa | Gold Wind | GE | SGRE | Vestas | GE | GW Option 1 | GW Option 2
P50 Generation | 31700000 | 29600000 | 34500000 | 36600000 | 36200000 | 33200000 | 29100000 | 33800000
P75 Generation | 30300000 | 28100000 | 32800000 | 35300000 | 34900000 | 31900000 | 26400000 | 30800000
P90 Generation | 28900000 | 26700000 | 31300000 | 34100000 | 33800000 | 30800000 | 24100000 | 28100000

## Slide 22: Project Feasibility Steps
Logistics Study
Topographic Survey
Geo Technical Study
Wind Resource Assessment
Geo Technical Study
Grid Interconnection
Wind Project Feasibility
Done
< 90 Days
>90 Days
Environmental Study

## Slide 23: BESS System

## Slide 24: Least Cost of Energy Solar PV – Wind - BESS
The Three blocks of Hybrid Power Plants shall be connected to the 132kV substation
The Power Capacity of the 132kV Substation should be 3x 300MVA step up transformer ( 33kV/132kV , 100MVA Transformers).
Each Hybrid Plant with BESS shall be connected to the independent transformer.
Triple circuit 132kV Transmission line shall evacuate the power with 100MW capacity each as shown in the layout earlier.
Area required for each block
  Wind - 2300 Acre
  PV – 50MW - 175Acres ( although as per configuration solar PV panels can be placed in same area as Wind Turbines)
  BESS – 2 acre of land (2.5-3.5MWh size of each container –Total 30-40 containers)
Case 3 Continued – Interconnection Arrangement

## Slide 25: Least Cost of Energy Solar PV – Wind - BESS
The estimated CAPEX cost of 100MW Wind Plant is USD 145million
The estimated CAPEX cost of 50MW Solar PV Plant is USD 23.6million USD
The estimated CAPEX cost of 50MW/100MWH BESS is USD 26.5million
Total estimated CAPEX cost per block is USD 195.1million
Grid Connection cost is estimated at USD 7 million
OPEX is estimated at USD 4 million
LCOE is estimated at Usc 4.4
LCOE in PKR equivalent is PKR 11.88 / kWh
Case 3 Continued – Interconnection Arrangement

## Slide 26: Least Cost of Energy Solar PV – Wind - BESS
Case 3 Continued – Interconnection Arrangement
Chart: Winters
| 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23
WIND Average Gross Power | 26.9043 | 28.0735 | 28.8731 | 30.2852 | 32.0564 | 31.507 | 31.1272 | 28.758 | 27.9123 | 19.3189 | 17.8782 | 18.5748 | 17.2474 | 15.1272 | 14.5827 | 16.2069 | 18.6038 | 23.3528 | 27.9156 | 29.4131 | 28.883 | 27.357 | 24.3081 | 25.8367
SOLAR Average Gross Power | -0.038 | -0.038 | -0.038 | -0.038 | -0.038 | -0.038 | -0.038 | 0.0010323 | 8.7634 | 17.6962 | 18.8114 | 19.2495 | 18.9692 | 18.8536 | 18.8373 | 18.2194 | 12.0206 | 1.4345 | -0.038 | -0.038 | -0.038 | -0.038 | -0.038 | -0.038
WIND+SOLAR Average Gross Power | 26.8663 | 28.0355 | 28.8351 | 30.2472 | 32.0184 | 31.469 | 31.0892 | 28.759 | 36.6757 | 37.0151 | 36.6896 | 37.8243 | 36.2166 | 33.9809 | 33.42 | 34.4263 | 30.6244 | 24.7873 | 27.8776 | 29.3751 | 28.845 | 27.319 | 24.2701 | 25.7987
Chart: Summers
| 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23
Wind | 40.5688 | 39.7976 | 38.5918 | 36.7345 | 35.3792 | 35.0422 | 35.8865 | 34.5923 | 34.5981 | 35.5967 | 35.8577 | 36.1627 | 35.6595 | 36.5073 | 36.8483 | 38.6785 | 41.5521 | 43.1142 | 45.2265 | 45.3073 | 43.6668 | 42.533 | 41.6474 | 40.7224
Solar | -0.038 | -0.038 | -0.038 | -0.038 | -0.038 | -0.038 | 2.3339 | 8.0994 | 12.424 | 14.8295 | 18.1599 | 17.7941 | 18.2794 | 18.2334 | 16.5971 | 14.9303 | 11.9768 | 8.04 | 2.4655 | -0.038 | -0.038 | -0.038 | -0.038 | -0.038
Hybrid | 40.5308 | 39.7596 | 38.5538 | 36.6965 | 35.3412 | 35.0042 | 38.2204 | 42.6917 | 47.022 | 50.4261 | 54.0177 | 53.9567 | 53.9389 | 54.7407 | 53.4454 | 53.6088 | 53.5289 | 51.1543 | 47.6919 | 45.2693 | 43.6288 | 42.495 | 41.6094 | 40.6844

## Slide 27: Least Cost of Energy Solar PV – Wind - BESS
In Hybrid Solar Wind Power Plants Shading is an important aspect during the siting.
The diagram below shows the configuration of installation.
The results of simplified analysis shows that less than 1% per month is lost to shading with a total sum of 2% per annum.
Shading on Solar PV arrays
Case 3 Continued – Interconnection Arrangement

## Slide 28: Way Forward:
Land:
BOR to be approached for issuance of Allotment Order;
BOR will submit the Case to Cabinet for approval;
Land Lease Fee be Submitted by SREC
SREC to obtain Funds from SEHCL

## Slide 29
Thankyou
Engr. Mehfooz Ahmed Kazi